## Consultation Responses
Compnay Name | Q1. Do you believe that the GC0137 Original Proposal better facilitates the Applicable Objectives? | Q2. Do you support the proposed implementation approach? | Q3. Do you have any other comments? | Q4. Do you wish to raise a Workgroup Consultation Alternative Request for the Workgroup to consider? | Q5. Do you believe it is appropriate specify GB Grid Forming as a non-mandatory requirement in the Grid Code and be accessed by future market arrangements rather than as a mandatory requirement? | Q6. Do you believe the current proposal is sufficiently flexible and facilitates a range of technologies? If not, please state why you feel this to be the case and what type of technologies have been excluded? | Q7. Do you believe the proposal will result in excessive equipment costs? This excludes development costs whilst recognising plant can be also be de-loaded? | Q8. Do you believe the proposed Grid Code proposals sit better in the Planning Code, Connection Conditions / European Connection Conditions and Compliance Processes / European Compliance Processes bearing in mind the proposals are non-mandatory or do you think it would be better to have a new standalone section | Q9. Do you support the approach of using the Grid Code to specify the minimum function performance requirements and a GB Grid Forming Best Practice Guide to provide further details? If not please state your reasons for not doing so? | Q10. The ESO do not believe that it is appropriate for traditional Synchronous Generators (GBGF-S) to meet some of the requirements – for example the submission of NFP Plots on the basis of their already proven features and the higher costs of submitting this data. Do you agree that this is a fair approach on the basis that it will only put costs up if they were mandated to do so? If not please state why you disagree
Siemens Energy | Yes | Yes | No | No | Yes | Yes | It depends on the final implementation of the source of energy. This includes the size and rating of the system. If it is a separate storage system, then there could potentially be significant additional costs depending on the final configuration. If the energy can be accessed via other means (e.g. energy from a separate AC network in the case of an interconnectors) and the interconnector is not required to overload, then there wouldn’t be significant equipment cost. | We would say that the European Connection Conditions are best placed to house the requirements given that similar services (e.g. FSM) are also described there.
GE Grid Solutions Ltd | Cannot comment on GC0141. Should this be a reference to GC0137? | Yes | Please refer to the 26 comments in Appendix 1 below. | No | Yes | Yes | No | No Comment
National Grid ESO | Yes | Yes | We have worked with many stakeholders as part of this work and would wish to note the extensive research many stakeholders have undertaken in particular some have undertaken full scale live trials to demonstrate the capability of the technology. | No | Yes – We believe this is the most appropriate and economical approach and is also technologically neutral. The approach taken, which would be combined with a future market, would enable developers to decide if they wished to participate in this market, it enables providers of conventional synchronous technologies to compete as well as newer technologies and also provides an additional revenue stream for a set of capabilities which have traditionally been provided for free. | Yes | No. The requirements are not mandatory so cannot expose developers to higher costs. The specification has been developed to be as flexible as possible including the option to de-load so we hope that any party wishing to provide this capability would not result in excessive costs, particularly in respect of the higher semiconductor ratings which may be required. | The ESO’s preference is to have the specification included in the European Connection Conditions with the data requirements in the Planning Code and Compliance Requirements in the European Compliance Processes. We are however relaxed on this issue and will await to see the feedback provided by other Stakeholders.
Enstore | No | Yes | I consider that two Edits are needed based on work carried out are the consultation was issued The proposed Edits are after the Specific Workgroup Consultation questions Specific Workgroup Consultation questions | No | Yes But the question is missing "to" before specify | Yes | No | No
Drax | Yes | Yes | Yes - see response proforma | No | Yes | Yes |  | It is better to have all requirements in the existing sections rather than moving then in to stand alone sections.
Vattenfall | N/A | Yes | Please see the response proforma | No | YES. Providing grid forming capability is an important service to the electricity grid similar to actual power supply and it should therefore be seen as a market regulated arrangement. It makes sense for developers to implement grid forming functionality in their converter design however the grid forming capability shall be non-mandatory. Developers will need to carryout internal assessment to decide if supplying grid forming capabilities are economically sensible for the individual project. The Grid Forming Capability should be implemented as a market regulated service with clear and generic (technology neutral) qualification requirements. It will also need to be clarified if some or all of the “Technical Performance Requirements”, will have to be met if a Generator/HVDC converter has opted to provide GB Grid forming services. | We agree that Grid Forming Capability should also include large scale HVDC Converter stations [as planned for the future connection of offshore windfarms]. However the OFTO regulatory framework will need to be changed to allow such large HVDC assets to participate in the proposed commercial market. Hybrid Power Plants [ie a combination of wind, solar, battery] could also be included as an aggregated unit to provide GB Grid Forming & blackstart. Black-start capability could also be one of the services that a large HVDC converter/windfarm could provide, and included in the “Technical Performance Requirements” | Yes we understand that there will be some extra cost for the equipment however Grid Forming is a critical next step to ensure GB grid stability as large synchronous machines are removed from the transmission system. However, to meet technical requirements for a Grid Forming converter, it is necessary to de-load a windfarm. In that case, a framework to compensate the loss in the revenue due to lost generation shall be established. For HVDC connected windfarms specifically this solution would need additional components and equipment offshore to provide the service. Energy storage at onshore HVDC (GBGF-I) may be needed to provide inertial power, although VSM0H (limited Inertia+Damping power; high Band Width requirements) are not precluded in Grid Code. Cost benefit in HPP may be better. Is it necessary to provide all the “Technical Performance Requirements”? Can some services eg phase jump, damping, vector shift control be provided as separate services, and you are paid for what you provide? | We think it should have its own standalone section where it is clear that it is non-mandatory to avoid confusion. How would the GBGF Grid Code be adapted to be included in the Network Restoration codes for the blackstart capability option (relaxations due to wind power fluctuations, eg for pumped hydro)? Will the definition of GBGF be the same in the context of blackstart, or instead, for example is Grid Leading behaviour preferred in the initial energization stage? In islanded operation, given that external grid is absent or weak, and may not have traditional Pf-QV coupling, so maybe that VSM based GF methods are not the best. Is this within scope of Grid Code? What rules apply in Grid Forming controls, since inertial response may not be the best approach in this instance, and may need to be adapted?
EDF | Faciliates Grid Code proposals a, b and c | Yes | None | No | It is appropriate to include non-mandatory technical requirements for GB Grid Forming in the Grid Code, with Grid Forming accessed by market arrangements. This will provide technology developers with a measure of guidance and confidence going forward. It is very important that Grid Forming market arrangements are swiftly put in place and that these arrangements are completely open and non-discriminatory for all existing and new plant and technologies that comply with the technical requirements. | The proposals must be drafted to facilitate the whole range of technologies. We are not aware of any excluded technologies at present | No response | A new standalone section of the Grid Code would be the most accessible area for these nonmandatory requirements.
Sygensys | There are improvements, but EMT models mentioned in GC0141 are part on international best practice for IBR modelling and are highly desirable. See later comments. | Yes | See more detailed comments at the end of this document. | No. I am happy to provide the informal comments at the end of this document. I hope some may be of interest to the workgroup. | I would suspect that making it mandatory, with a reasonable long introduction period, may give the lowest system operating costs and highest grid resilience. | The proposal allows a good degree of flexibility, but the current proposal makes no mention of the use of smart loads as a mechanism to address grid stability issues. This should be considered as part of the overall system analysis. See latter comments | No. The proposal is a good compromise between improved performance and minimal hardware costs. | No comment
Scottish Power Renewables | Yes - please see response proforma | Yes | Please see below annex. SPR will also support any comments made by SGRE in their submitted technical responses. | No | Yes - please see response proforma | SPR do believe the proposal is flexible enough for providers and facilitate a range of technologies. However, SPR support technical views of convertor-based technology providers are highlighting on this matter, particularly SGRE. SPR would also like to highlight that GB GF provides a number of benefits for the system operation that go beyond the usual recognised inertia capabilities. In order to incentivise the participation of a wider range of technologies, the remuneration incentive around GB GF should be flexible and remunerate each of these capabilities. Avoiding a black and white approach that may push back providers that are unable to fulfil the full extent of the specification will be critical for the success of the roll-out of GB GF. However, SPR understand these considerations may not be part of the scope of this proposal. | At the moment, SPR is still to understand the extent of the additional costs although that’s certainly subject to the time in which developers and technology providers decide to enable the capabilities (i.e. early stage of design, retrofit, etc.). SPR do think that any additional costs out of enabling the grid forming capabilities should be remunerated through market mechanisms that provide a signal and incentive to developers tp undertake changes in the designof their power plants. | As the proposal is for a non-mandatory services, SPR believe it would be better to have a new standalone section in the Grid Code similar to the Demand Response Services Code. This would make it consistent as a non-mandatory service and avoid confusions about the responsibilities on generators. | Yes, SPR support this approach and the creation of a Best Practice Guide | SPR understand there are inherent differences between GBGF-S and GBGF-I technologies and agree that some dynamical performance characteristics are already understood for GBGFS while not so much for GBGF-I. SPR also agree that would be inefficient and not cost effective to mandate testing /analysis to those plants with characteristics that are well understood. However, SPR would encourage NGESO to promote a level playing field between technologies and advocate for removing some preconceptions on GBGF-I technologies that could turn to be disadvantageous for the industry and its participants. SPR hope that NGESO would build the confidence on the performance on this technology along with supporting key technology players.
Statkraft UK Ltd | Yes | Yes | Please see below | No | Yes, it is entirely appropriate that for generators this is non-mandatory. Given the development cost, timescales and scale of HVDC converter developments, it would be appropriate to consider whether this should be mandatory for HVDC schemes. |  | With grid forming inverter technology, we recognise the need to provide simulations and / or additional test results. However, it should be recognised that as confidence in this type of technology grows, the additional simulations / test results may no longer be required. In particular, hardware tests to verify simulations may no longer be required. Further, EMT simulations may no longer be required, RMS simulations may be adequate. The new sections of the grid code should be reviewed at a set time (e.g. 2 years) after introduction to ensure that these simulations / tests are not adding unnecessary costs. | No comments received
SMA Solar Technology AG | Yes | Yes | Yes please find them in the table below, referring to the legal text (Annex 10) | No | Yes | Yes | For Storage Systems the costs are assumed to be moderate, depending on overload capability needed at the end in the market. For PV we expect additional costs due to storage needed, that depend strongly on the final plant specific requirements. | It's fine as it is proposed.
Siemens Gamesa |  | Yes |  |  | Probably, at least for now. Could be mandatory in future, but unlikely could ever be retrospectively applied | Yes | Not excessive due to this proposal, but the grid forming properties will have cost(s) associated with them. | unsure
SP Energy Networks | Yes | This modification deals with new technology that the industry as a whole is only beginning to understand. It seems likely that the minimum specification may need to be revised in the near future, so the working group might give some thought how best to implement this modification now while recognising possible future changes. | A specific issue that may need to be addressed in future revisions is the negative phase sequence impedance of converters and the effect on system unbalance, both in normal operating conditions and in response to faults or other disturbances. The proposed legal text is limited in what it says on this issue. The consultation document notes the requirement for models to be incorporated into the ESO’s software for power system analysis. It may be useful to also note that those same models will be shared with other transmission licensees, and that additional modelling information may be requested through the Bilateral Agreement. It may also be necessary to share models and data with third parties, as already provided for in industry codes, so it may be useful to explore the level of confidentiality that may be attached to the data being requested. | No | Yes | Yes | No response | These new requirements are likely to require revision and refinement in the near future as the industry comes to understand the implications and opportunities more fully. As such, a new standalone section may be better to allow further modification while minimising complex interaction with other parts of the Grid Code. | Yes. Future revisions seem likely and it will be easier to accomplish this in a Best Practice Guide. Details can be incorporated into Grid Code if appropriate once settled. | It is preferable for all parties to face the same requirements, irrespective of technology type, to help ensure a fair and open market for services. This is a non-mandatory technical specification and there is no expectation of retrospective application to existing synchronous generators. The issue should be explored further in the proposed Expert Group.
GE Renewable Energy | Yes | In general, we support the approach, especially the proposed non-mandatory requirements & service approach in this early phase of grid forming requirements in grid codes and technology development. Please also notice the provided comments, questions and Alternative Requests. | Please find our comments and questions below. On the Glossary - Definition of Voltage Jump Reactive Power: The definition of this parameter includes a dynamic requirement requesting instantaneous supply of voltage jump reactive power as a result of a voltage magnitude change. Background and intention of this dynamic requirement is unfortunately not fully clear. For other parameters like e.g. phase jump active power, dynamics are defined in the quite clear way that a response should start within less than 5 milliseconds. It is unfortunately unclear why is this kind of specification was not used for the voltage jump reactive power and a quantitative dynamic requirement would be appreciated. On the Glossary – Definition of Control Based in conjunction with ECP.A.3.9.6: The draft in conjunction with the provided guidance document provide quite clear information that a 5 Hz control bandwidth requirement shall be applied. Unfortunately, the draft does not provide details on quantitative acceptance criteria for meeting this requirement. It would be an important improvement and help to understand the tolerance around the 5 Hz control bandwidth limitation more clearly. On ECC.6.3.19.3 (vi): In general, the entire draft includes a lot of well- defined quantitative requirements. Unfortunately, the damping requirements for the active power output and reactive power output following a disturbance just refer to the term “adequately damped” without giving a clear definition what “adequately damped” shall quantitatively mean (e. g. minimum damping ratio). In general, we would appreciate if this ambiguity could be eliminated, but maybe there is some background information available why just the term “adequately damped” was used in this clause and not specified more in detail. On ECC.6.3.19.3 (viii): From reading this clause and the draft requirements in general it is not fully clear if the model structure shown in Figure 3.0 labeled “Typical Simulation Model” is a) the only one that shall become acceptable and must be supported by any technology or b) if this is an example and users / vendors have flexibility for providing an equivalent model of their Grid Forming Plant. Some clarification on this item would be appreciated. In general, we would like to strongly recommend keeping model structures in this early phase of grid forming technology implementation as open and flexible as possible. On Appendix ECP.A.3.9. The Appendix provides an outline about the compliance process but unfortunately does not include detailed information on a) how simulation and/or measurement results shall be assessed and on b) acceptance criteria. Assessing simulation and/or measurement results should be carefully considered as the performance parameters to be checked (“within less than 5 ms”) fall within the same time domain as a lot of other transient phenomena creating noise around the data of interest under assessment (switching transients, DC offsets, harmonics , etc.). And for acceptance criteria it can make a significant difference if performance and compliance get evaluated by assessing 1ms (“instantaneous”) values or RMS values (over 20ms) or floating 50ms average values, etc. Some information on how and when details on a) and b) shall be developed more in detail and published would be very helpful. | Yes, please find Workgroup Consultation Alternative Requests submitted together with this response. | Yes, we regard this implementation in this early phase of grid forming requirements in grid codes and technology development path as very positive. | We still see potential for more flexibility for the proposed services / required capabilities. I.e. it can make a difference if a grid forming plant shall be also capable to serve an islanded part of the grid completely on its own or in connection with other generation plants. Please also refer to the submitted Workgroup Consultation Alternative Requests. | The additional grid forming capabilities will do impact the costs of wind energy. A more detailed response could be provided if e.g., but not limited when more information on the method of delivery and other service / product related details are available. | As the new services related closely to the Connection Conditions et. al. and a lot of references are part of the proposal, we think that these new non-mandatory requirements sit well in this section.

## Summary of Responses
Theme | Key Points | Options | Outcome at Workgroup meeting
Does the Original Proposal better facilitate the Applicable Objectives | 7 respondants said Yes it better facilitates the applicable objective, and 1 responsdant said No and 6 were undecided. It is however unclear if the responses received were due to the error in the consultation question referring to GC0141 rather than GC0137.
Support for the implementation approach | Unanimous support for Implementation approach
Alternative solutions | No respondents wish to raise an alternative
GB Grid Forming (mandatory/non-mandatory) | Non-mandatory technical requirements will provide investment signals for new and existing projects via commercial markets. Mandatory with a reasonably long introduction period may give the lowest system operating costs and highest grid resilience. Non-mandatory is entirely appropriate for generators. But given development cost, timescales and scale of HVDC converter developments, it would be appropriate to consider being mandatory for HVDC schemes. The creation of a Best Practice Guide was suggested. Not affordable for developers to participate in competitive processes e.g. CfDs inclusive of costs as may compromise ability to secure CfD contracts. Given industry challenges/targets e.g. carbon zero 2025 & 2030 converter capacity deployment remuneration mechanisms should not compromise speed of decarbonisation. A non-mandatory requirement will encourage competition. | 1. Consider adding this into the Workgroup report 2. Does it need a alternative to be raised, if so by who? 3. Does the solution need changing? 4. Do we simply note it? | 1. Consider adding this into the Workgroup report.
Facilitation of GC technologies | Majority agree that the current proposal is sufficiently flexible and facilitates a range of technologies. Grid Forming Capability should also include large scale HVDC Converter stations. The OFTO regulatory framework will need to be changed to allow such large HVDC assets to participate in the proposed commercial market. Hybrid Power Plants [i.e. a combination of wind, solar, battery] could also be included as an aggregated unit to provide GB Grid Forming & black start. Consider smart loads as a mechanism to address grid stability issues. GB GF provides a number of benefits for the system operation that go beyond the usual recognised inertia capabilities. In order to incentivise the participation of a wider range of technologies, the remuneration incentive around GB GF should be flexible and remunerate each of these capabilities. Consideration of Synchronous Compensators - These would effectively (in terms of technology) be treatred in the same way as a Synchronous Generator | 1. Consider adding this into the Workgroup report 2. Does it need a alternative to be raised, if so by who? 3. Does the solution need changing? 4. Do we just note it? | 1. Consider adding this into the Workgroup report reflect points in the workgroup report and clarify that GF is potentially available for all plants and apparatus. (see notes KP)
Cost related to proposal | If it is a separate storage system, then there could potentially be significant additional costs depending on the final configuration. If the energy can be accessed via other means (e.g. energy from a separate AC network in the case of an interconnectors) and the interconnector is not required to overload, then there wouldn’t be significant equipment cost. The requirements are not mandatory so cannot expose developers to higher costs. The specification has been developed to be as flexible as possible including the option to de-load so we hope that any party wishing to provide this capability would not result in excessive costs, particularly in respect of the higher semiconductor ratings which may be required. To meet technical requirements for a Grid Forming converter, it is necessary to de-load a windfarm. In that case, a framework to compensate the loss in the revenue due to lost generation shall be established. For HVDC connected windfarms specifically this solution would need additional components and equipment offshore to provide the service. Energy storage at onshore HVDC (GBGF-I) may be needed to provide inertial power, although VSM0H (limited Inertia Damping power; high Band Width requirements) are not precluded in Grid Code. Cost benefit in HPP may be better. Can some services e.g. phase jump, damping, vector shift control be provided as separate services, and you are paid for what you provide? Any additional costs out of enabling the grid forming capabilities should be remunerated through market mechanisms that provide a signal and incentive to developers to undertake changes in the design of their power plants. The new sections of the grid code should be reviewed at a set time (e.g. 2 years) after introduction to ensure that these simulations / tests are not adding unnecessary costs. | 1. Consider adding this into the Workgroup report 2. Does it need a alternative to be raised, if so by who? 3. Does the solution need changing? 4. Do we just note it? | 1. Consider adding this into the Workgroup report no change to solution, reflect;1. recomendation section within the report. 2. change to other industry codes, STC and offshore environment. 3. How large is the potential market. (see notes KP)
Standalone section into GC/embedded in other sections | Existing (x4): ECCs as similar services (FSM) are described there; ECCs for Spec, PC for data reqs, ECPs for Compliance. New standalone section to emphasise non-mandatory (x3) | 1. Consider adding this into the Workgroup report 2. Does it need a alternative to be raised, if so by who? 3. Does the solution need changing? 4. Do we ignore it? | 1. Consider adding this into the Workgroup report make reff to anyone offering a black start has GF capability and additional requirements specified in the black start contract. preference to ensure grid forming is integrated into the exisiting parts of the GC (e.g. PC, CC, ECC, ECP) rather than a standalone section. Black start contract will need to reflect the extra elements Parked and factored into the wider black start strategy
Sufficient flexibility of proposal/facilitation of technologies? Why/why not? | GBGF should also include large HVDC converters (but requires OFTO framework changes to facilitate commercial market participation). Hybrid power plants could be included as aggregated unit for GBBF/BS. BS capability could be a service & included in Technical Performance Requirements. Proposal should not exclude any technologies (n.b. this counts as a yes - MB). Good degree of flexibility but smart loads should be considered for grid stability also. Other views on commercial approach beyond scope of this mod, but noted accordingly. | 1. Consider adding this into the Workgroup report 2. Does it need a alternative to be raised, if so by who? 3. Does the solution need changing? 4. Do we just note it? | 1. Consider adding this into the Workgroup report. Compliance - MA, clear steer from NG Timeframes Sampling
Areas of Techncial detail | Numerous comments have been received on the technical detail and wording. It is beyond the scope of this spread sheet to cover each of these but we will be looking at them in detail and considering how to take them forward. The aim is to address the detailed elements as part of the Expert Group through the best practice guide and keep the Grid Code as high level as possible. A number of issues were raised on testing and the resolution of recorded signals. This will also be addressed as part of the ongoing work to improve the Grid Code spec. | Detailed comments will be addressed on a case by case basis and factored into the revised specificaiton or covered through the Expert Group